## Sheet1
Utility Needs for E163 at ESB | [7 empty] | E.Colby, D.Palmer, D.Walz, R.Cassel, S.Gold, R.Noble, 9/17/2001(original)
Expanded 12/11/2002 to include more precise locations of loads.
Updated 8/29/03 with new mod/rf powers.
Description | Electrical Load | Air Heat Load | Water Heat | Clean | Load Location | Voltage | Current | Water | Water type | Gases | NOTES
| Watts | Watts | Load Watts | Power? | (see note below) | Volts | Amps | GPM | LCW/Chill
1. Laser Room (500 sq. ft.) | [10 empty] | Located within Northeast Area ESB
Fluorescent Lighting (0.5 W/s.f.) | 250 | 250 |  | no | d | 110 | 3
Computer+Monitor | 500 | 500 |  | no | plug | 110 | 5
1 Rack of equipment | 1000 | 1000 |  | YES | rack1 | 110 | 10
Tsunami 3960-M1S | 200 | 200 |  | YES | plug | 110 | 2
Millenia VsP & Power Supply | 1000 | 1000 |  | YES | plug | 110 | 10
C-option Lock-to-Clock | 200 | 200 |  | YES | plug | 110 | 2
TSA-25 Amplifier |  | 50
Evolution X |  | 50
LAB-170-10 |  | 50
Misc Loads | 500 | 500 |  | YES | plug | 110 | 5
| Electrical | Reject to Air | To Water
Total Loads: | 3650 | 3800 | 0
Clean Power | 2900
Dirty Power | 750
Service Circuits:
6 110V, SP | [6 empty] | 5 |  |  |  | Mean Circuit Load 700 W, total 20 outlets reqd.
1 208 V, TP | [6 empty] | 25
2. Loads External to Laser Room
HVAC | 380 |  | 4180 | no | disconnect | 480/277 | 20 | 45 | LCW |  | EER=10, 20 A service for future margin
HEPA | 500 | 500 |  | no | breaker | 110 | 5
Evolution Power Supply | 1650 | 1600 |  | no | plug | 110 | 15
LAB-170 Power Supply | 5100 |  | 5000 | no | plug | 208 | 25 |  |  |  | To NesLab Chiller
Chiller for Tsunami | 1000 | 1000 |  | no | plug | 110 | 10
Chiller for Evolution | 1000 | 1000 |  | no | plug | 110 | 10
Chiller for LBA-170-10 | 2500 |  | 2500 | no | plug | 208 | 12 | 10 | LCW |  | NesLab HX-75W
1 Rack of equipment | 1000 | 1000 |  | YES | rack2 | 110 | 10
| Electrical | Reject to Air | To Water
Total Loads: | 13130 | 5100 | 11680
Clean Power | 1000
Dirty Power | 12130
Service Circuits:
6 110 V, SP | [6 empty] | 10 |  |  |  | Mean Circuit Load 700 W
4 208 V, SP | [6 empty] | 25
1 480 V, TP | [6 empty] | 25
3. RF Photoinjector | [10 empty] | Located within Upstream NLCTA Enclosure
Avg. max. photoinjector power is 500 W.
Cooling for RF Gun | 1000 |  | 1500 | no | disconnect | 208/230 | 16 | 20 | LCW |  | Surplus TeK-Temp TKD-250 with high margin
3 db coupler load cooling |  |  | 500 |  |  |  |  | 2 | LCW
Solenoid Power Supply | 5000 |  |  | no | disconnect | 187/265 | 20 |  |  |  | LT-860 Lambda PS
Cooling for Solenoid |  |  | 5000 |  |  |  |  | 10 | LCW |  | Use existing NLCTA solenoid water
To move pneumatic actuators | [9 empty] | 70-100 psi air
Ion Pump Power Supplies | 1000 | 1000 |  | no |  | 110 | 10 |  |  |  | Four 20 l/sec, Two 200 l/sec
| Electrical | Reject to Air | To Water
Total Loads: | 7000 | 1000 | 7000
Clean Power | 0
Dirty Power | 7000
Service Circuits:
5 110 V, SP | [6 empty] | 5 |  |  |  | 20 outlets required
2 110 V | [6 empty] | 20
2 208 V, TP | [6 empty] | 20
4. Modulator and Power Supplies | [10 empty] | Located at South Wall, NLCTA
3 Control Racks:
HV Power Supply | 6619 | 993 |  | no | rack 3 powered | 208 TP | 25 |  |  |  | 5U of rack space (1U above and below)
Core Reset P.S. | 48 | 7 |  | no | rack 3 powered | 110 | 8 |  |  |  | 1U of rack space (1U above and below)
Core Bias P.S. | 107 | 16 |  | no | rack 3 powered | 110 | 8 |  |  |  | 1U of rack space (1U above and below)
Klystron Solenoid P.S. | 5098 | 765 |  | no | rack 3 powered | 208 TP | 20 |  |  |  | 5U of rack space (1U above and below)
Cathode Heater P.S. | 498 | 135 |  | no | rack 4 powered | 208 TP | 5 |  |  |  | 2U of rack space (1U above and below)
Ion Pump Power Supplies | 500 |  |  | no | rack 4 powered | 110 | 5
Misc. other loads | 500 | 500 |  | no | rack 4 powered | 110 | 5
Solid State Amplifier | 300 |  | 300 | YES | rack 5 powered | 110 | 5 | 2 | LCW
Oscillator/Timing/LLRF | 500 | 200 | 300 | YES | rack 5 powered | 110 | 5 | 3 | P.I. Chiller? |  | 5U of rack space (1U above and below)
VME/Controls | 300 | 300 |  | YES | rack 5 powered | 110 | 5
Misc. clean loads | 500 | 500 |  | YES | rack 5 powered | 110 | 10
Modulator:
IGBT Stack, core reset Cooling |  |  | 541 |  |  |  |  | 2 | LCW
| Electrical | Reject to Air | To Water
Total Loads: | 14970 | 3416 | 1141
Clean Power | 1600
Dirty Power | 13370
Service Circuits:
5 110 V, SP | [6 empty] | 5
2 208 V, TP | [6 empty] | 25
5. Klystron System | [10 empty] | Located at South Wall, NLCTA
5045 klys is 47% eff. 5126W yields 2409 avg. rf output.
Klystron/Waveguide Ion Pumps |  | 500
Solenoid cooling |  |  | 4333 | [7 empty] | Solenoid, PT and Collector cooling
Pulse Transformer cooling |  |  | 454 | [7 empty] | in series; turbulent flow.
Collector cooling |  |  | 4126 |  |  |  |  | 20 | LCW |  | Collector Max 5126 W at full Modul. Power w/o rf
Isolator Load Cooling |  |  | 5126 |  |  |  |  | 15 | LCW |  | Turbul. Flow, High Margin - Nominally <1 kW dissipated.
| Electrical | Reject to Air | To Water
Total Loads: | 0 | 500 | 8913
Clean Power | 0
Dirty Power | 0
Service Circuits:
2 110 V, SP | [6 empty] | 5
6. Inside 650 s.f. Shielding Enclosure | [10 empty] | Located at northeastern ESB
Fluorescent Lighting (0.5 W/s.f.) | 325 | 325 |  | no | d | 110 | 5
1 HEPA Unit | 500 | 500 |  | no | plug | 110 | 5
Heater Tapes (occassional) | 5000 | 5000 |  | no | plug | 110 | 50 |  |  |  | Use Welding outlet in NE corner ESB, 100 A, 480V
Spectrometer |  |  | 20000 |  |  |  |  | 4 | LCW
Bend Dipoles |  |  | 2000 |  |  |  |  | 1 | LCW
Quads (12 @ 100 W each) |  | 1200
Steering Magnets |  | 1000
Turbo Pumps |  |  | 1000 |  |  |  |  | 0.5 | LCW
Ion pumps |  | 2000
To vent structures | [9 empty] | 10 SCFH LN2
To move pneumatic actuators | [9 empty] | 60-90 psi air
| Electrical | Reject to Air | To Water
Total Loads: | 825 | 5025 | 23000
Clean Power | 0
Dirty Power | 825
Service Circuits:
10 110 V, SP | [6 empty] | 5 |  |  |  | Mean Circuit Load 700 W, 40 outlets required
1 208 V, SP | [6 empty] | 20
1 480 V, TP | [6 empty] | 40
7. Loads External to Shielding Enclosure
Quad and bend supplies | 3200 |  |  | no | rack6 powered | 110 | 30 | 2 | LCW |  | If HEPL design
Spectrometer Supply | 20000 |  |  | no | disconnect | 480 | 50 | 4 | LCW
Steering Magnet Supplies | 1000 |  |  | no | rack6 powered | 110 | 10
Ion Pump Supplies | 2000 |  |  | no | rack7 powered | 110 | 20
Turbo Pump Power Supplies | 1000 |  |  | no | rack7 powered | 110 | 10
IR thermal stabilization chiller | 1000 | 1000 |  | no | rack7 powered | 110 | 10
Control Equipment | 1000 | 1000 |  | YES | rack8 powered | 110 | 10
Diagnostic Rack | 1000 | 1000 |  | YES | rack8 powered | 110 | 10
| Electrical | Reject to Air | To Water
Total Loads: | 30200 | 3000 | 0
Clean Power | 2000
Dirty Power | 28200
Service Circuits:
12 110 V, SP | [6 empty] | 5 |  |  |  | Mean Circuit Load 1000 W
1 208 V, SP | [6 empty] | 20
1 480 V, TP | [6 empty] | 60 |  |  |  | Attached to cut-off switch
8. Loads in DAQ Trailer | [10 empty] | Use Power Connection Outside ESB
HVAC | 1000 | 1000 |  | no | disconnect | 110 | 10
2 Racks @ 500W each | 1000 | 1000 |  | YES | rack9 rack10 | 110 | 10
5 Computers | 2500 | 2500 |  | no | plug | 110 | 30
| Electrical | Reject to Air | To water
Total Loads: | 4500 | 4500 | 0
Clean Power | 1000
Dirty Power | 3500
Service Circuits:
8 110 V, SP | [6 empty] | 5 |  |  |  | Mean Circuit Load 700 W
9. Future ORION Low Energy Hall |  | NOT CONSIDERED IN PRESENT COST ESTIMATES | [8 empty] | Located outside east wall of ESB
Internal:
Fluorescent Lighting (0.5 W/s.f.) | 800 | 800 |  | no |  | 110 | 10
HEPA Unit (2) | 1000 | 1000 |  | no |  | 110 | 10
Heater Tapes (occassional) | 5000 | 5000 |  | no |  | 110 | 50 |  |  |  | Use Welding outlet in NE corner ESB, 100 A, 480V
Spectrometer |  |  | 20000 | no |  |  |  | 4 | LCW
Bend Dipoles |  |  | 2000 | no |  |  |  | 1 | LCW
Quads (12 @ 100 W each) |  | 1200 |  | no
Steering Magnets |  | 1000 |  | no
Turbo Pumps |  |  | 2000 | no |  |  |  | 1 | LCW
Ion Pumps |  | 6000 |  | no
To vent structures | [9 empty] | 10 SCFH LN2
to move pneumatic actuators | [9 empty] | 60-90 psi air
| Electrical | Reject to Air | To Water
Total Internal Loads: | 1800 | 10000 | 24000
Internal Service Circuits:
20 110 V | [6 empty] | 5 |  |  |  | Mean Circuit Load 700 W, 40 outlets required
3 208 V, TP | [6 empty] | 20
1 480 V, TP | [6 empty] | 40
External:
Quad and Bend Supplies | 3200 |  |  | no |  | 110 | 30 | 2 | LCW
Spectrometer Supply | 20000 |  |  | no |  | 480 | 50 | 4 | LCW
Steering Magnet Supplies | 1000 |  |  | no |  | 110 | 10
Ion Pump Supplies | 6000 |  |  | no |  | 110 | 60
Turbo Pump Power Supplies | 2000 |  |  | no |  | 110 | 20
IR thermal stabilization chiller | 1000 | 1000 |  | no |  | 110 | 10
Control Equipment | 2000 | 2000 |  | YES |  | 110 | 20
Diagnostic Racks | 2000 | 2000 |  | YES |  | 110 | 20
| Electrical | Reject to Air | To Water
Total External Loads: | 37200 | 5000 | 0
Clean Power | 4000
Dirty Power | 33200
External Service Circuits:
12 110 V, SP | [6 empty] | 5
1 208 V, SP | [6 empty] | 20
1 480 V, TP | [6 empty] | 60
| Electrical | To Air | To Water |  |  |  |  | Flow
Total E163 Loads (items 1- 7) | W | W | W |  |  |  |  | GPM
| 69775 | 18041 | 51734 |  |  |  |  | 140.5
Clean Power | 7500
Dirty Power | 62275
Total Feeder (items 1-9) | 113275 |  |  | 480V service amps: |  | 235.9896
Clean Power | 12500
Dirty Power | 100775 |  |  |  | Notes:
[5 empty] | d | distributed load (lighting)
[5 empty] | plug | 110 or 208 brought to recepticles
[5 empty] | disconnect | power brought to a dedicated disconnect switch
[5 empty] | rackn | name of rack
[5 empty] | rack powered | power for item taken from rack power
[5 empty] | breaker | item wired directly into breaker